Calculation Formulas for Solar and BESS

# Unit Conversions

| Unit | Conversion |
| --- | --- |
| 1 MW | 1,000 kW |
| 1 MWh | 1,000 kWh |
| 1 Cr | ₹10,000,000 |
| 1 MU | 1,000,000 kWh |

# Solar Generation and Energy Split

Generation (kWh/yr) = Solar capacity (MW) × 1,000 × Specific yield (kWh/kWp)

Excess = Generation × Daytime excess percentage

Self-consumed = Generation − Excess

Example: 10 × 1,000 × 1,800 = 18,000,000 kWh = 18 MU/yr.
At 60% excess: 10.8 MU excess and 7.2 MU self-consumed.

# BESS Sizing and Charging

BESS power = Solar capacity × selected power percentage

BESS energy = BESS power × selected duration

Maximum annual charging = BESS energy × 1,000 × cycles/year

Eligible excess = Excess × excess-to-recover percentage

Actual charging = MIN(Eligible excess, Maximum annual charging)

Delivered energy = Actual charging × round-trip efficiency

Excess absorbed (%) = Actual charging ÷ Excess × 100

Example: 25% × 4 h: 2.5 MW, 10 MWh.
Maximum charging = 10 × 1,000 × 365 = 3,650,000 kWh = 3.65 MU. Since excess is 10.8 MU, actual charging is 3.65 MU. At 95% efficiency, delivered energy is 3,467.5 MWh; absorption is 33.8%, displayed as 34%.

# CAPEX and O&M

Solar CAPEX = Solar MW × solar CAPEX (Cr/MW)

BESS CAPEX = BESS MWh × BESS CAPEX (Cr/MWh)

Total CAPEX = Solar CAPEX + BESS CAPEX

Solar O&M = Solar CAPEX × 1%

BESS O&M = BESS CAPEX × 2%

Example: Solar CAPEX = ₹50 Cr, BESS CAPEX = ₹25 Cr, total = ₹75 Cr. Solar and BESS O&M are ₹0.50 Cr/yr each.

# Annual Savings

Solar gross savings (Cr/yr) = Self-consumed kWh × Grid tariff ÷ 10,000,000

Solar-only net savings = Solar gross savings − Solar O&M

BESS energy savings = Delivered kWh × (Grid tariff + Evening ToD premium) ÷ 10,000,000

Demand savings = BESS MW × 1,000 × Demand relief % × Demand charge × 12 ÷ 10,000,000

Incremental BESS net savings = BESS energy savings + Demand savings − BESS O&M

Solar + BESS net savings = Solar-only net savings + Incremental BESS net savings

Example: Solar-only net = ₹9.58 Cr/yr. BESS energy savings = ₹5.89475 Cr/yr; demand savings = ₹2.70 Cr/yr; incremental BESS net = ₹8.09475 Cr/yr. Total solar + BESS net = ₹17.67475 Cr/yr, displayed as ₹17.67 Cr/yr.

# Payback, Compliance, and Transformer

Solar-only payback = Solar CAPEX ÷ Solar-only net savings = 5.2 years

Solar + BESS payback = Total CAPEX ÷ Solar + BESS net savings = 4.2 years

BESS standalone payback = BESS CAPEX ÷ Incremental BESS net savings = 3.1 years

Payback improvement = Solar-only payback − Solar + BESS payback = +1.0 years

Required storage = Solar MW × applicable storage floor (MWh/MW). At 1 MWh/MW: 10 MWh, so the selected 10 MWh is compliant.

Allowed rooftop capacity = Transformer MVA × 70% = 7 MW. Transformer overage = Solar MW − allowed capacity = 3 MW.

ROI = Solar + BESS net savings ÷ Total CAPEX × 100 = 23.57%.

## Note

Banking-charge note: The ₹4/kWh banking and standby input is currently excluded from the savings equations; it is not subtracted from BESS energy savings.